Check if the Wiring is Correct

Start of VF Terminal Control Mode Commissioning

P1-01= Motor power

P1-01= 电机功率

Restore factory parameters (PP.01=1)

P1.02= Motor voltage

P1.02= 电机电压

P1.03= Motor current

P1.03= 电机电流

Input motor nameplate parameters

P1.04= Motor frequency

P1.04= 电机频率

P1.05= Motor speed

P1.05= 电机转速

Motor parameter input completed

电机参数输入完成

P1.37=1 Static tuning

Troubleshoot according to fault codes; contact the manufacturer if unresolved

If a fault is reported

Press the confirm key; the operation panel displays ARUN and flashes. Then press the RUN key; the drive enters tuning state. (After tuning is completed, the drive operation panel automatically returns to parameter display state)

Tuning steps

Start motor tuning

开始电机调谐

Tuning completed

If the rotation direction is incorrect

Check if the motor rotation direction is correct

Modify parameter P0.9=0/1 or after power - off, swap any two motor wires, then power on and retune (Retuning is mandatory; direct operation is not allowed)

Method

Adjust the panel potentiometer to set the frequency to 2, press the run key, and check if the motor rotation direction is correct

P0.10 = Set maximum frequency according to motor power
P0.12 = Set upper - limit frequency according to motor power

Rotation direction correct

1. Modify command source parameter P0.02=1, select command source (terminal command)
2. Modify main frequency source parameter P0.03=2 (corresponding to AI1), (3 corresponding to AI2), (4 corresponding to AI3)